LESSON 12

PROTECTIVE SYSTEMS

OUTLINE

Objectives

Introduction

Detection Systems (NFPA 1001: 4-5.1)

Sprinkler Systems (NFPA 1001: 3-3.13, 4-5.1)

Sprinklers and Life Safety (NFPA 1001: 3-3.13)

Sprinkler Head Design and Operation (NFPA 1001: 3-3.13, 4-5.1)

Types of Sprinkler Systems (NFPA 1001: 3-3.13, 4-5.1)

Sprinkler System Connections and Piping (NFPA 1001: 3-3.13, 4-5.1)

Control Devices for Sprinkler Systems (NFPA 1001: 3-3.13, 4-5.1)

Returning Sprinkler Systems to Service (NFPA 1001: 3-3.13)

Standpipe Classifications (NFPA 1001: 3-3.9)

Standpipe System Connections and Piping (NFPA 1001: 3-3.9, 
3-3.13, 4-5.1)

Alarms for Standpipes and Sprinklers

Fire Department Sprinkler and Standpipe Operations (NFPA 1001: 3-3.9, 3-3.13)

Other Protective Systems (NFPA 1001: 4-5.1)

Lessons Learned

Key Terms

Review Questions

Endnotes

Suggested Readings

CLASS ASSIGNMENT

Prior to this lesson:	Read Firefighter's Handbook, Chapter 12, 
pages 293-320

Length:	4 hours, 30 minutes

Equipment/Supplies:	Course outline

Transparency masters--Chapter 12

PowerPoint Presentation--Chapter 12

Overhead projector, slide projector, or LCD display

Sprinkler heads, wedges, and sprinkler tongs

OBJECTIVES

After completing this lesson, students should be able to:

- Identify the value of protective systems in protecting life and property.

- Identify and explain the operation of the various types of detection systems in protecting life and property.

- Explain and recognize the types of sprinkler heads and how they operate.

- Identify the various types of sprinkler systems and the components of each type.

- Identify the piping arrangements of sprinkler systems and connections.

- Demonstrate how to connect to a fire department connection.

- Identify control valves for systems and explain their operation.

- Explain the methods used to return a sprinkler system to service.

- Demonstrate techniques for stopping a flowing sprinkler head.

- Identify standpipe classes and types of systems.

- Identify piping and connections for standpipe systems.

- Demonstrate how to connect supply and attack lines to standpipe 
connections.

- Identify alarm systems for protective systems.

- Explain fire department procedures at protective properties.

- Identify other protective systems, their components, and the benefits and hazards.

INTRODUCTION

Firefighter's Handbook, page 295

Time: 10 minutes

Key Points

- Protective systems help protect lives and property by detecting and/or suppressing fires.

- Suppression systems are devices that help firefighters in controlling fires.

- Suppression systems are also called auxiliary appliances.

- Some detection systems require people to activate the alarm. Others can detect a fire almost at its ignition and sound an alarm.

- Sprinklers and standpipes are the two main suppression systems.

- Most suppression systems use water. However, dry and wet chemicals, inerting gases, and halogenated agents are also available.

DETECTION SYSTEMS

Firefighter's Handbook, pages 295-299

Time: 30 minutes

Key Points

- Detection systems discover the fire or other problem and notify people of the problem.

- Some detection devices are part of a fire suppression system, and others activate suppression systems.

- Detection systems should also be connected to a fire alarm system.

People or Manual Systems

- People can alert other building occupants and can call the fire department after discovering a fire.

- Some buildings are equipped with a manual fire alarm system that requires a person to discover the fire and then pull a lever or push a button.

- Street box systems are also manual fire alarm systems.

- Manual systems suffer from two typical problems.

- The first is that if they are to work, a person must be present, awake, and alert to discover the fire and then activate the system.

- The second problem is that many manual fire detection systems are local only. They will alert any building occupants but will not summon any additional help.

Heat Detectors

- Heat detectors operate by detecting the heat of a fire at a fixed temperature or as the rising temperature builds at a rapid rate.

- Heat detectors are slow to detect fire, and therefore should not be used for life safety.

- Heat detectors can be the spot type, which covers just one area, or the line type, which covers a larger area.

- There are several types of heat detectors available.

Smoke Detectors

- Smoke and toxic gases are the leading killers of people in the home.

- Smoke detectors are permanently wired, battery operated, or a combination of hard wiring with a battery backup.

- Ionization detectors use a radioactive element that emits ions into the chamber.

- When smoke enters the chamber, the flow of ions to the electrode changes and an alarm is activated.

- Ionization detectors are spot type devices that are inexpensive and are very quick to react.

- Photoelectric detectors use two different methods to detect the smoke of a fire.

- A light obscuration detector has a light beam aimed at a light sensor.

- A light-scattering detector operates by having a light beam aimed at the end of the chamber with a light sensor in an angled-off chamber.

Gas Detectors

- Gas-sensing detectors are designed to detect the presence of a certain gas or gases prior to reaching a concentration that can cause danger.

- Gas detectors can be permanently mounted devices or portable units.

- Fire departments carry gas detectors to check for flammable gases, carbon monoxide, other hazardous materials, and the oxygen content in the air.

Flame Detectors

- There are three types of flame detection devices: ultraviolet (UV), infrared (IR), or a combination ultraviolet-infrared (UV-IR) detector.

- These extremely rapid detectors are designed to protect petroleum and chemical facilities where fast and high temperature fires can occur.

- Ultraviolet flame detectors detect the radiation of high-intensity flaming fires by detecting the light waves emitted in the UV spectrum, which is below the visual light wavelengths.

- Infrared flame detectors detect the infrared radiation of a fire using a photocell, which is above the visual light wavelengths.

- Combined ultraviolet-infrared flame detectors are used to rapidly detect the flames of a fire but without the false alarm problems of the other type of detectors.

SPRINKLER SYSTEMS

Firefighter's Handbook, page 299

Time: 10 minutes

Key Points

- Sprinkler systems are designed to automatically distribute water through sprinklers that are placed at set intervals on a system of piping.

- Most sprinkler heads detect the heat of a fire and begin to apply water directly over the source of the heat.

- The NFPA has published standards for the installation of sprinkler systems and their inspection and maintenance.

SPRINKLERS AND LIFE SAFETY

Firefighter's Handbook, pages 299-300

Time: 15 minutes

Key Points

- Sprinkler systems were originally designed in the late 1800s to protect property.

- Sprinkler systems are highly effective. Most malfunctions are a result of human action such as improper maintenance or turning off the water supply.

- In 1975, the first standard on residential sprinklers was developed.

- Residential sprinklers are designed with the focus on life safety more than to protect property.

- Sprinkler systems are not totally effective for life safety in some types of fires.

- Slow burning and smothering fires produce fatal quantities of smoke without generating enough heat to activate the system.

- Protecting against all situations is impossible, but residential sprinkler systems, combined with an effective smoke detection system, allow maximum life safety.

SPRINKLER HEAD DESIGN AND OPERATION

Firefighter's Handbook, pages 300-303

Time: 25 minutes

Key Points

- Sprinkler heads are the key component of the system.

- More important are the heat-sensitive parts that usually detect heat and apply water to the fire.

- Sprinkler heads come in many designs, which affect performance.

- Old style sprinklers, which were manufactured up to the 1950s, deflected the majority of the water toward the ceiling to further break up its patterns.

- The new style or standard sprinklers have a much even flow across the coverage area and do not bounce water off the ceiling.

- Standard sprinklers are marked with SSU (Standard Sprinkler Upright) or SSP (Standard Sprinkler Pendent) on the deflector.

- Upright sprinklers have the head vertically above the piping with the deflector at the top.

- Pendents have the head suspended below the piping with the deflector at the lowest point.

- The design of sidewall sprinklers allows them to be placed near the wall.

- The operation of a sprinkler head begins with the fire's heat raising the temperature of the sprinkler head and its fusible element to its fusing point.

- There are three types of fusible elements.

- The first is a fusible link, which has a metal or solder that melts at a fixed temperature.

- The second is a bulb filled with a liquid, leaving only a small air bubble, which expands and bursts at a fixed temperature.

- The third is a chemical pellet that melts or bursts and the levers holding the cap then fall out, allowing water to flow.

- A newer innovation is an on/off head that operates at a fixed temperature.

TYPES OF SPRINKLER SYSTEMS

Firefighter's Handbook, pages 303-307

Time: 30 minutes

Key Points

- Specialty sprinkler systems include some combination-type sprinkler systems and systems that cannot meet the standards for some reason.

- Even if a system does not completely meet a standard, it provides a higher measure of protection than if no protection were available.

- Fire departments using special systems should become familiar with their limitations.

Wet Pipe Systems

- A wet pipe sprinkler system has automatic sprinklers attached to pipes with water under pressure all the time.

- The wet pipe system is the simplest sprinkler system in design and operation.

- The alarm line piping usually has a retard chamber that acts to prevent false alarms from a sudden pressure surge in the water supply.

- A wet pipe system has three more valves: a control valve, the main drain, and an inspector test valve.

Dry Pipe Systems

- In a dry pipe system, air under pressure replaces the water in the system to protect against freezing temperatures.

- When a sprinkler head is fused by heat, air is first discharged.

- As the air pressure drops below the pressure of the supply water, the clapper valve is opened and locked.

- Dry pipe systems are slower to activate.

- Many systems have an exhauster or accelerator to speed up the operation of the dry pipe valve.

- Dry pipe systems are used in unheated buildings, buildings that refrigerate or freeze materials, and in outdoor applications where freezing temperatures occur.

- The dry pipe system is more complex in design than the wet pipe system, and is also harder to restore.

Deluge Systems

- Deluge systems are designed to protect areas that may have a fast spreading fire.

- All of its sprinkler heads are already open, and when the system operates water flows to all heads, allowing total coverage.

- The system uses a deluge valve that opens when a separate fire detection system senses the fire and sends a signal to trip the valve open.

- Deluge systems are found in aircraft hangers, manufacturing facilities, petroleum handling facilities, and other highly hazardous locations.

Preaction Systems

- Preaction systems are similar to the dry pipe and deluge system.

- This system has closed piping and heads with air under little or no pressure, but the water does not flow until signaled open from a separate fire detection system.

- Preaction systems are used in areas where the materials protected are of high value and water damage would be expensive, such as computer rooms and historical items.

Residential Systems

- Residential sprinkler systems are smaller, more affordable versions of wet or dry pipe sprinkler systems.

- They are designed to control the level of fire involvement so that residents can escape.

- Residential systems use a check valve, water flow alarms, and drains.

- Some residential alarms use antifreeze to protect all or part of the system.

SPRINKLER SYSTEM CONNECTIONS AND PIPING

Firefighter's Handbook, pages 307-309

Time: 20 minutes

Key Points

- The connections and piping for a sprinkler system provide the water from its source to the heads, and they comprise most of the system.

- Depending on the requirements of the system and the water source, a fire pump may be included.

- A fire department siamese connection is a secondary water source, which allows pumpers to supplement the water supply.

- The fire department connection is usually piped in past the main control valve and can supply the system even if the main control valve is closed.

- Another required valve in most systems is a backflow preventor.

- The system may have other control valves and check valves, and will have a water control valve if connected to a public water supply.

- Next in line is the main control valve, which is of the wet, dry, deluge, or preaction type as described earlier.

- Above that is the riser, which feeds the mains that feed the cross mains to the branch lines.

- Tamper alarms alert the alarm company whenever someone operates the valve, and unauthorized valve operations are quickly checked to prevent criminal acts.

- Firefighters should be able to properly connect a supply line to a fire department connection for either a sprinkler or a standpipe.

- When connecting to a siamese, a firefighter should choose the outlet on the far left first. This will allow better access for using a spanner wrench to tighten the coupling.

CONTROL DEVICES FOR SPRINKLER SYSTEMS

Firefighter's Handbook, page 309

Time: 10 minutes

Key Points

- The three main control devices for sprinkler and standpipe systems are the outside stem and yoke valve (OS&Y), the post indicator valve (PIV), and the wall indicator valve (WIV).

- The valves have either a butterfly or gate valve type.

- The OS&Y valve has a wheel on a stem housed in a yoke or housing.

- PIVs and WIVs are similar. One is mounted on a wall, while the other is mounted on a post in the ground.

- Some water control valves may also be of the non-indicating type.

RETURNING SPRINKLER SYSTEMS TO SERVICE

Firefighter's Handbook, pages 310-312

Time: 15 minutes

Key Points

- In the past, fire departments regularly restored sprinkler and other protective systems to service for building owners.

- Today many departments no longer provide this service.

- Fire departments either stop the flowing head or shut the system down.

- Firefighters must understand how to properly shut down either individual heads or the entire system.

- When the fire is completely out, the first step to restore the system is to shut down any pumper supplying the system.

- If the system is to be restored immediately or a large number of heads have opened, either the main sprinkler or a sectional valve should be shut down and drained.

- After the sprinkler heads are replaced, the valves must be reset or reopened.

- The simplest way to stop a sprinkler is to insert sprinkler tongs, wooden wedges, or dowel rods in the frame and orifice of the head.

- The other way to shut off the water flow from open sprinklers is to shut down either the main sprinkler valve or a floor or sectional valve.

- Once the system is shut down and drained, the heads may be replaced.

- When refilling a system, fill the system slowly to prevent damaging the system.

- If the system cannot be restored to service, the fire department can request a fire watch.

STANDPIPE CLASSIFICATIONS

Firefighter's Handbook, pages 312-313

Time: 15 minutes

Key Points

- Standpipe systems are designed to allow firefighters to fight fires in large buildings by prepiping water lines for fire streams through the building.

- Some systems allow both occupants and firefighters to use the system.

- Tunnel systems, such as subway systems, and shopping malls have horizontal standpipe systems.

- Standpipe systems are classified according to the type of intended user, and each class sets requirements for volume and size of outlets.

- Class I systems are designed to be used by the fire department or trained personnel.

- Class II systems are designed for use by untrained building occupants, and have a 1 ½ - inch hoseline attached with a minimum flow of 100 gpm.

- Firefighters using this system should replace the hoseline with one of their own.

- A Class III system can be used by either a trained or untrained person, but the system must meet the Class I requirements for flow.

- Any of these systems may have a pressure-regulating device.

- The types of standpipe systems are differentiated based on their water supply.

- An automatic wet pipe system has a water supply.

- Automatic dry and semiautomatic dry pipe systems use dry pipe until a hose station is opened.

- A semiautomatic system requires an activation valve to be opened manually.

- The manual dry pipe is completely dry and relies on the fire department connection for water supply.

STANDPIPE SYSTEM CONNECTIONS AND PIPING

Firefighter's Handbook, pages 313-314

Time: 20 minutes

Key Points

- Standpipe systems can range from very simple to highly complex ones with multiple connections, risers, water supply sources, and many outlets on each floor.

- The components of a standpipe system include piping, outlets with hose and other attachments, the valves, the fire department connection, and any monitoring devices.

- Piping includes the riser or risers and any attachments needed.

- The outlets are usually placed in the building stairwell or may be a wall-mounted cabinet.

- Any pressure-regulating devices would be attached to the outlet.

- Standpipe valves are similar to the types used on sprinkler systems, including gate valves of various types and check valves, with the addition of hose valves at the outlets.

- The fire department connection(s) is an inlet or siamese device with the protective caps and a raised letter sign marked "Standpipe."

ALARMS FOR STANDPIPES AND SPRINKLERS

Firefighter's Handbook, page 314

Time: 10 minutes

Key Points

- Alarms and monitoring systems are found in most sprinkler systems and many standpipe systems.

- Sprinkler systems are both fire detection and suppression devices.

- Standpipe systems used by building occupants should be monitored to assure the fire department has been notified.

- The movement of a gate valve may electronically or mechanically activate standpipe systems.

- Water flow alarms are also electrical or mechanical.

- A monitoring alarm company notifies the fire department about fires, but its own personnel will respond to tamper alarms.

FIRE DEPARTMENT SPRINKLER AND STANDPIPE OPERATIONS

Firefighter's Handbook, pages 314-315

Time: 30 minutes

Key Points

- Standpipe and sprinkler systems, plus any other protective system, should be part of the fire department's overall strategic plan to provide fire protection for its community.

- The fire department must survey its hazards and also its resources, both public and private.

- The property owner does maintenance, the fire prevention bureau does inspections, and fire companies do the preplanning.

- Preplanning identifies hazards and resources, and some key resources are protective systems.

- For standpipe and sprinkler systems, fire company personnel should know the type of system, the location of connections, two water supply points, and the location of key valves.

- Standpipe operations start with establishing a water supply to the fire department connection with a minimum of one hoseline.

- The pump operator should immediately charge the standpipe system.

- The first arriving unit should have its personnel check the annunciator panel and then go to the reported location of the fire.

- Personnel should have full personal protective equipment, standpipe pack, and forcible entry equipment.

- Sprinkler system operations start with having the information on the building and its systems.

- The first step on arrival is still to establish a water supply to the fire department connection.

- The system should be charged immediately if it is combined with a standpipe system.

- Personnel should advance hoselines into the fire area and conduct extinguishment and overhaul operations.

OTHER PROTECTIVE SYSTEMS

Firefighter's Handbook, pages 315-317

Time: 15 minutes

Key Points

- Many other protective systems are used today.

- The firefighter needs to understand the most common types of protective systems.

- Fire departments responding to the more complex systems should ensure all personnel are familiar with them.

Local Application and Hood Systems

- The local application system is a common type of protective system.

- Local application means that the system is designed to protect only a certain, or local, portion of the building.

- Most local application systems use dry or wet chemical agents.

- Higher temperature cooking units and oils have created the need for 
a new Class K classification. These systems also use dry or wet 
chemicals.

Total Flooding Systems

- Total flooding systems are used to protect an entire area, room, or 
building.

- Total flooding systems can use carbon dioxide or other inert gases, halogenated or clean agents, dry chemicals, or foam as extinguishing agents.

- There are hazards associated with each type of application with which firefighters and building personnel should be familiar.

WRAP-UP

Time: 15 minutes

Key Points

- Protection systems are devices designed to either automatically detect or suppress a fire.

- Firefighters need to understand the value and operation of these systems to protect their communities.

- Sprinkler systems are used for detection and suppression and can apply water or foam to extinguish a fire.

- The four main types of systems are wet pipe with water in the pipes, dry pipes, deluge systems, and preaction systems.

- Each type of system uses a different type of alarm valve, but many of the other features are similar.

- Standpipe systems facilitate manual fire suppression in which people do the firefighting.

- Standpipes supply water in large buildings.

- Building occupants can also use some standpipe systems.

- Standpipe operations require careful coordination of firefighters due to the size of the building involved.

- Other protective systems detect fires and apply other extinguishing agents to fires in proximity to the hazard or fill an entire area.

- Restaurants and kitchens usually have a hood system protecting the cooking areas, while other systems are used to protect high hazards or high value items.

- Firefighters must understand how specialized protective systems work and any hazards of the agents used by these systems.

Assignment

- Read Chapter 13 in Firefighter's Handbook, pages 321-344

- Optional: Complete Firefighter's Handbook Workbook, Chapter 13

Instructor Preparation

PowerPoint Presentation--Chapter 13

Transparency masters--Chapter 13

Overhead projector, slide projector, or LCD display